TENDER SPECIFICATIONS (for main items)

1 AEL-GPRE. Unit.

The trainer includes the following modules:

• N-ALI01. Industrial Power Supply.

Supply voltage: 400 VAC, 3PH+N+G.

ON-OFF removable key.

Output voltage connections:

Three-Phase + Neutral: 400 VAC.

Single-Phase: 230 VAC.

Three-Phase supply hose with IP44 3PN+E 32A 400V connecting plug.

Differential magnetothermal, 4 poles, 25A, 300mA AC 6KA.

• N-ERP-PGC01. Generator protection relay module.

Generator protection relay module.

Single-phase supply voltage: 230 VAC.

“Island grid/parallel grid” control switch.

“Local/remote” control switch.

Manual control switches of the relay:

SW1, emergency stop.

SW2, automatic start of the motor-generator group.

SW3, protections reset pushbutton.

SW4, generator frequency control activation.

SW5, 52G1 synchronization circuit breaker closure manual permission.

State light indicators.

Alarm light indicators.

Synchronization safety key.

Emergency stop pushbutton.

SUB-D signals connector of 62 pins.

ON-OFF switch.

Connection terminals.

The N-ERP-PGC-01 generator protection relay:

Enables to connect up to 16 diesel generators in parallel-island with distribution of active and reactive load and start/stop in function of the load

demand.

Enables to connect one generator in parallel with the grid.

Enables different switches control modes, such as opening, closing and synchronization.

Includes analogical outputs to control voltage and frequency regulators available in the market.

Three-phase measurement of the grid and generator voltage.

Three-phase measurement of the generator intensity and power.

Single-phase measurement of the grid intensity.

Protections:

Generator: max/mín-voltage (59/27), max/min-frequency (81O/U), voltage asymmetry, dead bus detection, overload (32), unbalance load

(46), reverse power/reduce (32R/F), overcurrent time define curve (50/51), inverse time overcurrent (IEC255), fault ground (50N/51N), phases,

breakers fault.

Motor: over/sub speed (12).

Mains: max/min-voltage (59/27), max/min-frequency (81O/U), vector surge.

• N-VVCA5K. Speed control of the 5KW motor.

AC 5KW motors control module.

Three-phase supply voltage: 400VAC + N.

Rated power: 5KW.

Motor speed control potentiometer.

ON-OFF control switch.

Local/remote control switch.

Signals connector SUB-D of 62 pins.

ON-OFF switch.

Connection terminals.

• N-AVR/P. Automatic voltage regulator.

Generator excitation regulator.

Local/remote control switch.

Manual/automatic control switch of the excitation in local mode.

Excitation current manual control potentiometer.

ON-OFF switch.

Connection terminals.

Communication connector SUB-D of 62 pins.

• N-EALD. Network Analyzer Unit with Computer Data Acquisition.

ON-OFF switch.

Supply voltage: 400 VAC.

Input terminals: Input connection with the measurement point.

Output terminals: Output connection with the measurement point.

Digital outputs: Three digital outputs are used for pulses or alarms, or for combining both.

RS-485 Communication port.

Fuses: 3x10 A.

Network Analyzer Display. It shows:

Active, reactive and apparent power.

Active, reactive and apparent energies.

Lines and phase currents.

Line and phase voltages.

Frequencies.

Power Factor.

• N-CAR35T3. Three-phase bank of commutable resistors module.

Three phase bank of commutable resistors module.

Three sliding load switches.

Three three-phase commutable banks of resistors of 150 ohms.

ON-OFF switch.

3 stages x(3x1kW)

• N-ERP-MF01. Digital faults simulator module.

Faults injection module.

Fault type preselector:

Three-phase fault.

Two-phase fault.

Two-phase to ground fault.

Single-phase fault.

ON-OFF switch.

Connection terminals.

• GMG4.5K3PH. 4.5KW generator-motor group.

Motor-generator group coupled in an aluminium frame with wheels.

Rated power of the generator: 4.5 KVA.

Stator rated I: 6.5 A.

Excitation rated I: 4 A.

RPM: 3000 r.p.m.

Motor rated power I: 5 KVA.

Rated I: 7.2 A.

RPM: 3000 r.p.m.

• N-ERP-PDF01. Differencial protection relay.

Differential protection relay module.

Single-phase supply voltage: 230 VAC.

Light indicator of TRIP.

Differential protection.

DB9 RS-232 communication connector.

SUB-D signals connector of 62 pins.

ON-OFF switch.

Connection terminals.

Characteristics:

It protects two terminals transformers, generators, reactances and other power devices using a combination of differential, instantaneous and

“inverse-time” overcurrent elements. The safety of the differential diagram is obtained by the following actions:

Dual-slope percentage reduction.

Second and forth harmonic blocking.

Fifth harmonic blocking for transformer overexcitation.

CT and transformers connection compensation.

• N-REP. Rotor earth-fault protection module.

Nominal voltage: 400 V.

Relay voltage: 24 V.

Contacts: 1 n.o., 1 n.c.

Contact rating: 10 A.

Test button.

Reset button.

Two earth-fault signal lamps.

Additional generation group:

• N-ERP-PGC01. Generator protection relay module.

Generator protection relay module.

Single-phase supply voltage: 230 VAC.

“Island grid/parallel grid” control switch.

“Local/remote” control switch.

Manual control switches of the relay:

SW1, emergency stop.

SW2, automatic start of the motor-generator group.

SW3, protections reset pushbutton.

SW4, generator frequency control activation.

SW5, 52G1 synchronization circuit breaker closure manual permission.

State light indicators.

Alarm light indicators.

Synchronization safety key.

Emergency stop pushbutton.

SUB-D signals connector of 62 pins.

ON-OFF switch.

Connection terminals.

The N-ERP-PGC-01 generator protection relay:

Enables to connect up to 16 diesel generators in parallel-island with distribution of active and reactive load and start/stop in function of the load

demand.

Enables to connect one generator in parallel with the grid.

Enables different switches control modes, such as opening, closing and synchronization.

Includes analogical outputs to control voltage and frequency regulators available in the market.

Three-phase measurement of the grid and generator voltage.

Three-phase measurement of the generator intensity and power.

Single-phase measurement of the grid intensity.

Protections:

Generator: max/mín-voltage (59/27), max/min-frequency (81O/U), voltage asymmetry, dead bus detection, overload (32), unbalance load

(46), reverse power/reduce (32R/F), overcurrent time define curve (50/51), inverse time overcurrent (IEC255), fault ground (50N/51N), phases,

breakers fault.

Motor: over/sub speed (12).

Mains: max/min-voltage (59/27), max/min-frequency (81O/U), vector surge.

• N-VVCA5K. Speed control of the 5KW motor.

AC 5KW motors control module.

Three-phase supply voltage: 400VAC + N.

Rated power: 5KW.

Motor speed control potentiometer.

ON-OFF control switch.

Local/remote control switch.

Signals connector SUB-D of 62 pins.

ON-OFF switch.

Connection terminals.

• N-AVR/P. Automatic voltage regulator.

Generator excitation regulator.

Local/remote control switch.

Manual/automatic control switch of the excitation in local mode.

Excitation current manual control potentiometer.

ON-OFF switch.

Connection terminals.

Communication connector SUB-D of 62 pins.

• GMG4.5K3PH. 4.5KW generator-motor group.

Motor-generator group coupled in an aluminium frame with wheels.

Rated power of the generator: 4.5 KVA.

Stator rated I: 6.5 A.

Excitation rated I: 4 A.

RPM: 3000 r.p.m.

Motor rated power I: 5 KVA.

Rated I: 7.2 A.

RPM: 3000 r.p.m.

• All necessary cables to realize the practical exercises are included.

The complete unit includes as well:

Advanced Real-Time SCADA.

Open Control + Multicontrol + Real-Time Control.

Specialized EDIBON Control Software based on LabVIEW.

Projector and/or electronic whiteboard compatibility allows the unit to be explained and demonstrated to an entire class at one time.

Capable of doing applied research, real industrial simulation, training courses, etc.

Remote operation and control by the user and remote control for EDIBON technical support, are always included.

Totally safe, utilizing 4 safety systems (Mechanical, Electrical, Electronic & Software).

Designed and manufactured under several quality standards.

Optional ICAI software to create, edit and carry out practical exercises, tests, exams, calculations, etc.

Apart from monitoring user’s knowledge and progress reached.

This unit has been designed for future expansion and integration. A common expansion is the EDIBON Scada-Net (ESN) System which enables multiple students to simultaneously operate many units in a network.

2 AEL-GPRE/CCSOF. Computer Control + Data Acquisition + Data Management Software:

The three softwares are part of the SCADA system.

Compatible with the industry standards.

Flexible, open and multicontrol software, developed with actual windows graphic systems, acting simultaneously on all process parameters.

Management, processing, comparison and storage of data.

It allows the registration of the alarms state and the graphic representation in real time.

Open software, allowing the teacher to modify texts, instructions. Teacher’s and student’s passwords to facilitate the teacher’s control on the student, and allowing the access to different work levels.

This unit allows the 30 students of the classroom to visualize simultaneously all the results and the manipulation of the unit, during the process, by using a projector or an electronic whiteboard.

3 Cables and Accessories, for normal operation.

4 Manuals:

This unit is supplied with 7 manuals: Required Services, Assembly and Installation, Control Software, Starting-up, Safety, Maintenance & Practices Manuals.

*	References 1 to 4 are the main items: AEL-GPRE +  AEL-GPRE/CCSOF + Cables and Accessories + Manuals are included in the minimum supply for enabling normal and full operation.

EXERCISES AND PRACTICAL POSSIBILITIES TO BE DONE WITH THE MAIN ITEMS

1.- Study of generation power systems.

2.- Analysis of the measurements of the power flows of the synchronous generator.

3.- Analysis of the active and reactive power of the synchronous generator.

4.- Automatic synchronization maneuvers of synchronous generator with the mains.

5.- Study of the synchronous generator in island operation mode.

6.- Study of the synchronous generator in grid parallel operation mode.

7.- Study of excitation/voltage regulation of synchronous generator in island mode.

8.- Study of turbine regulation (frequency control) in island mode.

9.- Study of excitation/voltage regulation of synchronous generator in parallel grid operation mode.

10.- Study of turbine regulation (frequency control) in parallel grid operation mode.

11.- Study of the power factor regulation of synchronous generator in parallel grid operation mode.

12.- Setting of time overcurrent protection.

13.- Setting of unbalance load protection.

14.- Setting of reverse power protection.

15.- Setting of overvoltage and undervoltage protection.

16.- Setting of PID voltage.

17.- Setting of PID frequency voltage.

Additional practical exercises possibilities with the optional modules:

For differential protection relay studies (with optional module “N-ERP-PDF01”):

18.-Calculating protection operating values.

19.-Fault recognition within the protection range.

20.-Testing tripping and reset for faults occurring inside and outside the protection range.

21.-Disconnection and de-excitation of the generator.

22.-Measurement of the operating (pick-up) currents of the protection device for symmetrical and asymmetrical faults.

23.-Comparison of measured values to set values.

For rotor earth-fault relay studies (with optional module “N-REP”):

24.-Connection and testing of earth-fault relay.

25.-Setting different rotor earth-faults.

Additional practical exercises possibilites with the optional SCADA (AEL-GPRE/CCSOF).

26.- Remotely control of generation power systems.

27.- Analysis with the SCADA software of synchronous generator power flows.

28.- Analysis with SCADA software of active and reactive power of synchronous generator.

29.- Remotely control of manual synchronization of synchronous generator with the mains.

30.- Remotely control of automatic synchronization of synchronous generator with the mains.

31.- Remotely control of synchronous generator in island grid operation mode.

32.- Remotely control of synchronous generator in parallel grid operation mode.

33.- Remotely control of excitation/voltage regulation of synchronous generator in island mode.

Other possibilities to be done with this Unit:

34.- Many students view results simultaneously.

To view all results in real time in the classroom by means of a projector or an electronic whiteboard.

35.- The Computer Control System with SCADA allows a real industrial simulation.

36.- This unit is totally safe as uses mechanical, electrical and electronic, and software safety devices.

37.- This unit can be used for doing applied research.

38.- This unit can be used for giving training courses to Industries even to other Technical Education Institutions.

- Several other exercises can be done and designed by the user.

Tender Specifications (for optional items)

a) Technical and Vocational Education configuration

5 AEL-GPRE/ICAI. Interactive Computer Aided Instruction Software System.

This complete software package consists of an Instructor Software (EDIBON Classroom Manager –ECM-SOF) totally integrated with the Student Software (EDIBON Student Labsoft –ESL-SOF). Both are interconnected so that the teacher knows at any moment what is the theoretical and practical knowledge of the students.

-ECM-SOF. EDIBON Classroom Manager (Instructor Software).

ECM-SOF is the application that allows the Instructor to register students, manage and assign tasks for workgroups, create own content to carry out Practical Exercises, choose one of the evaluation methods to check the Student knowledge and monitor the progression related to the planned tasks for individual students, workgroups, units, etc...so the teacher can know in real time the level of understanding of any student in the classroom.

Innovative features:

User Data Base Management.

Administration and assignment of Workgroup, Task and Training sessions.

Creation and Integration of Practical Exercises and Multimedia Resources.

Custom Design of Evaluation Methods.

Creation and assignment of Formulas & Equations.

Equation System Solver Engine.

Updatable Contents.

Report generation, User Progression Monitoring and Statistics.

-ESL-SOF. EDIBON Student Labsoft (Student Software).

ESL-SOF is the application addressed to the Students that helps them to understand theoretical concepts by means of practical exercises and to prove their knowledge and progression by performing tests and calculations in addition to Multimedia Resources. Default planned tasks and an Open workgroup are provided by EDIBON to allow the students start working from the first session. Reports and statistics are available to know their progression at any time, as well as explanations for every exercise to reinforce the theoretically acquired technical knowledge.

Innovative features:

Student Log-In & Self-Registration.

Existing Tasks checking & Monitoring.

Default contents & scheduled tasks available to be used from the first session.

Practical Exercises accomplishment by following the Manual provided by EDIBON.

Evaluation Methods to prove your knowledge and progression.

Test self-correction.

Calculations computing and plotting.

Equation System Solver Engine.

User Monitoring Learning & Printable Reports.

Multimedia-Supported auxiliary resources.

b) Multipost Expansions options

6 Mini ESN. EDIBON Mini Scada-Net System.

EDIBON Mini Scada-Net System allows up to 30 students to work with a Teaching Unit in any laboratory, simultaneously.

The Mini ESN system consists of the adaptation of any EDIBON Computer Controlled Unit with SCADA integrated in a local network.

This system allows to view/control the unit remotely, from any computer integrated in the local net (in the classroom), through the main computer connected to the unit.

Main characteristics:

- It allows up to 30 students to work simultaneously with the EDIBON Computer Controlled Unit with SCADA, connected in a local net.

- Open Control + Multicontrol + Real Time Control + Multi Student Post.

- Instructor controls and explains to all students at the same time.

- Any user/student can work doing "real time" control/multicontrol and visualisation.

- Instructor can see in the computer what any user/student is doing in the unit.

- Continuous communication between the instructor and all the users/students connected.

Main advantages:

- It allows an easier and quicker understanding.

- This system allows you can save time and cost.

- Future expansions with more EDIBON Units.

The system basically will consist of:

This system is used with a Computer Controlled Unit.

- Instructor’s computer.

- Students’ computers.

- Local Network.

- Unit-Control Interface adaptation.

- Unit Software adaptation.

- Webcam.

- Mini ESN Software to control the whole system.

- Cables and accessories required for a normal operation.